## Sheet1
Parameter	Name	Scope	Range	Default v1.5	Default v1.6	Default v1.6.1	Current Value
P00	Power-down recovery function	0:off;1:on	0:off;1:on	1	1	1	1
P01	Input Power: Single / three phase selection	0:Single-phase 1:Three-phase	0:Single-phase power Three- 0 phase power	0	0	0	0
P02	Power frequency	0 : 50HZ ; 1 : 60HZ	5:50HZ; 1:60HZ	1	1	1	1
P03	Heat source selection	0:ground source; 1:air source	0;ground source 1:Air source	1	1	1	1
P04	Heating temperature control method	0:Method 1; 1:Method 2	0:Method 1 : 1:Method 2	0	0	0	0
P05	Defrost method selection	0:Method 1; 1:Method 2	0:Method 1 : 1:Method 2	0	0	0	0
P06	FREECOOLING validation	0:valid; 1:invalid	0:valid; 1:invalid	1	1	1	1
P07	Frequency control method	0:Method 1; 1:Method 2	0:Method 1; 1:Method 2	0	0	0	0
P08	DHW validation G1	0:valid; 1:invalid	0:valid; 1:invalid	1	1	1	1
P09	Air conditioning and heating validation	0:valid; 1:invalid	0:valid; 1:invalid	0	0	0	0
P10	Air conditioning and Cooling validation	0:valid; 1:invalid	0:valid; 1:invalid	0	0	0	0
P11	DHW hot water temp hysteresis	2~15°C,minus hysteresis	2~15°C,minus hysteresis	2°C	2°C	2°C	2
P12	AC temp hysteresis	2~15°C,minus hysteresis	2~15°C,minus hysteresis	2°C	2°C	2°C	2
P13	Ambient temp to start heating of Heating temp control Method 2	-10~15°C(Higher than the set ambient temperature before starting)	-10~15°C(When ambient temp is higher than this temp it can start)	7°C	-	-	7
P14	Indoor target temperature	10~28°C	10~28°C	21°C	-	-	21
P15	buffer tank highest temp	35~55°C	35~55°C	45°C	-	-	45
P16	buffer tank lowest temp	15~30°C	15~30°C	25°C	-	-	25
P17	Water temperature adjustment scope	1~5°C	1~5°C	2°C	-	-	2
P18	water temp adjust interval time	2~300min	2~300min	120min	-	-	120
P19	longest counting period time	6~48H	6~48H	24H	-	-	24
P20	target water temp corrected Value	-2~5°C	-2~5°C	0°C	-	-	0
P21	ambient temp correction factor	0.1~2.0	0.1~2.0	0.75	-	-	75
P22	Counting starting ambient temp	-7~15°C	-7~15°C	7°C	-	-	7
P23	Frequency control method	0:Method 1; 1:Method 2	0:Method 1; 1:Method 2	0°C	-	-	0
P24	Low-frequency ambient temperature	30~10°C(A)	30~10°C(A)	15°C	-	-	15
P25	High-frequency ambient temperature	-20~8°C(B)	-20~8°C(B)	0°C	-	-	0
P26	The lowest operating frequency	10~50%(C)	10~50%(C)	30.00%	-	-	30
P27	The maximum operating frequency	55~100%(D)	55~100%(D)	100.00%	-	-	100
P28	Frequency limit pressure	2.00-4.50MPa	2.0-4.5MPa	3.70MPa(37)	-	-	37
P29	Cancel limit frequency pressure	2.00-4.50MPa	2.0-4.5MPa	3.40MPa (34)	-	-	34
P30	fan motor Category	0=AC fan, 1=EC fan1, 2=EC fan 2	0=AC Fan, 1=EC Fan1, 2= EC Fan2	1	1	1	1
P31	Maximum speed of the fan	10-100 ( 100 show1 00% )	1-10(10=100%)	100	100	100	100
P32	Heating fan speed control temperature difference	2~15°C	2~15°C	1°C	1°C	1°C	1
P33	Cooling Fan speed control Temperature difference	5~18°C	5~18°C	12°C	6°C	6°C	6
P34	Defrost method selection	0:Method 1; 1:Method 2	0:Method 1; 1:Method 2	0	0	0	0
P35	defrost starting temp	-5~5°C	-5~5°C	-1°C	-1°C	-1°C	-1
P36	defrost interval time multiple rate	0:Not defrost;1;2;3;4: (interval X 4)	0:Not defrost;1;2;3;4: 1 (interval X 4)	1	1	1	1
P37	The first defrost interval	15~99minu(1st interval after repower on)	15~99minute(1st interval after 35 repower on)	35	35	35	35
P38	defrost exist temp	10~35°C	10~35°C	30°C	30°C	30°C	30
P39	Set value of △	3~8(B)	3~8(B)	5	-	-	5
P40	Ambient temp correction value of △	(5~50)/100(C)	(5~50)/100(C)	10/100	-	-	10
P41	ambient temp correction multiple rate	1~5(D)	1~5(D)	1	-	-	1
P42	water temp correction value of △	(5~50)/100(E)	(5~50)/100(E)	10/100	-	-	10
P43	water temp correction multiple rate	1~5(F)	1~5(F)	1	-	-	1
P44	Minimum allowed △	(1~100)/100(G)	(1~100)/100(G)	30	-	-	30
P45	Allowed defrost coil temperature	-20~0°C(H)	-20~0°C(H)	-6°C	-	-	-6
P46	Allowed the defrost time	1~10min(I)	1~10min(I)	3min	-	-	3
P47	hot water frequency limitation	2~10,max frequency 20~100%	2~10= max frequency 20~100%	100	100	100	10
P48	AC heating AU mode highest temp	30~50°C	30~50°C	45°C	45°C	45°C	45
P49	AC Heating AU mode offset temperature	-10~10°C	-10~10°C	0°C	0°C	0°C	0
P50	solenoid valve function parameters	0=G3 seasonal valve,1=G3 solar valve	0= G3 is seasonal valve,1=G3 is solar valve	0	0	0	0
P51	C4 Water pump type selection	0=AC Water pump,1=EC Water pump	0=AC Water pump,1=EC Water pump	1	1	1	1
P52	water pump working mode	0=Not stop, 1=stop after reaching target temp)2=start 1 minute after each stopping of 15 minutes)	0=Not stop, 1=stop after reaching target temp)2=start 1 minute after each stopping of 15 minutes)	0	0	0	0
P53	EC Water pump C4 Minimum speed	40-80%	40-80% 40, “80” during startup	80	40	40	40
P54	C5 Water pump type selection	0=AC Water pump,1=EC Water pump	0=AC Water pump,1=EC Water pump	0	0	0	0
P55	DHW e-heater activated ambient temperature	-20~20°C	-20~20°C	0°C	0°C	0°C	0
P56	Electric heating function	0=electric heating, 1=the second heat source	0=electric heating, 1=the second heat source	0	0	0	0
P57	AC e-heater activated ambient temperature	-20~20°C	-20~20°C	0°C	0°C	0°C	0
P58	2nd heat source starting air temp	-30~15°C	-30~15°C	-15°C	-15°C	-15°C	-15
P59	AC anti-freezing temperature	-15~5°C	-15~5°C	3°C	3°C	3°C	-15
P60	Virus killing interval days	7~99day	7~99 day	99	99	99	99
P61	Start virus killing time	1~24hour	1~24 hour	1	1	1	1
P62	Virus killing holding time	5~99minu	5~99 Min	5	5	5	5
P63	Target temperature of virus killing	55~80°C	55~80°C	55°C	55°C	55°C	55
P64	AC water flow switch type selection	0=Water flow switch 1=flow meter	0=Normal Water flow switch 1=Water flow meter switch	1	1	1	1
P65	AC minimum water flow (Sets P5)	9-80L/m	9-80L/m	8	8	8	3
P66	Water source Water flow switch type selection	0=Water flow switch	0=Normal Water flow switch 1=Water flow meter switch	0	-	-	0
P67	The lowest water flow of water source	9-80L/m	9-80L/m	9	-	-	3
P68	air source heat pump FREECOOLING function start ambient temp	-16~20°C	-16~20°C	5°C	5°C	5°C	5
P69	FREECOOLING function additional Temperature difference to start full free cooling. (compressor stops)	3~15°C	3~15°C	5°C	5°C	5°C	5
P70	water source side anti- freeze temp	-20~5°C	-20~5°C	2°C	-	-	2
P71	Cooling Maximum set temperature	15~35°C	15~35°C	25°C	25°C	25°C	25
P72	Heating maximum set temperature	25~55°C	25~55°C	55°C	55°C	55°C	55
P73	DHW The highest set temperature	25~60°C	25~60°C	60°C	60°C	60°C	60
P74	Debugging fixed operating frequency	10~100 HZ	10~100 HZ	50HZ	50HZ	50HZ	50
P75	run setting frequency	0= Manual frequency, 1= Auto frequency	0= Manual frequency, 1= Auto frequency	1	1	1	1
P76	EEV manually open degree (heating)	70~480	70~480	250	200	200	200
P77	EEV manually open degree (cooling)	70~480	70~480	250	250	250	250
P78	EEV control mode	0=No,1=table list,2=manually, 3=automatically	0=No,1=table list,2=manually, 3=automatically	3	3	3	3
P79	target overheat degree (heating)	-5~10°C	-5~10°C	-1°C	-1°C	-1°C	-1
P80	target overheat degree (cooling)	-5~10°C	-5~10°C	2°C	2°C	2°C	2
P81	night mode validation	0= no start, 1= start	0= no start, 1= start	0	0	0	0
P82	night mode starting point	0-23(for relative time)	0-23(for relative time)	22	22	22	22
P83	night mode ending point	0-23(for relative time)	0-23(for relative time)	6	6	6	6
P84	High-pressure protection settings	2.50~5.00MPa	2.50~5.00MPa	4.5	-	-	450
P85	Low-pressure protection settings	0.01~1.00MPa	0.01~1.00MPa	0.2	-	-	20
P86	High-pressure protection stop hysteresis	0.20~1.50MPa	0.20~1.50MPa	0.5	-	-	5
P87	Low-pressure protection stop hysteresis	0.01~1.00MPa	0.01~1.00MPa	0.2	-	-	20
P88	Model selection	0~255	0~255	4	4	4	4
P89	Electronic expansion valve manual opening	70~480	70~480	200	-	-	200
P90	Electronic expansion valve control mode	0=No, 1=table list, 2=manually 3=automatically	0=No, 1=table list, 2=manually 3=automatically	0	-	-	0
P91	Condensation temperature correction value	-5~10°C	-5~10°C	5°C	-	-	5
P92	Whether to use high and low pressure transmitter	-5~10°C	-5~10°C	5°C	-	-	5
P93	Target air temperature coefficient	0.75~1.15	0.75~1.15	0.95	-	-	0.95
P94	Whether to use high and low pressure transmitter	0=Disabled 1= Enable	0= N/A 1= Enable	0	0	0	0
P95	C4 Control the temperature difference (°C)	2~8	2~8	5	5	5	5
P96	Compressor Manufacturer		Mitsubishi				0x101:MITSUBISHI
P97	Manual Virus Killing		NO	0	0	0	0x101:MITSUBISHI
P98	Reset Factory parameter		NO	0	0	0	0x101:MITSUBISHI
P99	Manufacture of compress2						101

	Reboot required ! ! !						0x101:MITSUBISHI
	Communication protocol						Omron
	Baud rate						9600